## Slide 1: DC Fast Charge System Impact Study and Distributed Charging Resources
Southern California Edison EPIC Project Summaries
Energy Storage Technologies & Applications Conference
Jordan Smith, P.E.
12 April 2019

## Slide 2: Agenda
Overview of DCFC SI project
Procedures and Measurements
Summary of Findings
Mitigation Measures
Overview of Distributed Charging Resources Project

## Slide 3: Southern California Edison Overview
SCE
Service
Territory
50,000 square-mile service area
5 million customer accounts
14 million residents
Infrastructure
  1.4 million poles
  700,000 transformers
  103,000 miles of T&D lines
Rate base growth driven by:
  Safety and reliability
  Distribution Resources Plan
  Transmission growth, renewables
  State environmental policy
  Electric Vehicle charging and Energy Storage

## Slide 4: SCE Pomona Labs – EV Technical Center
  Established in 1993
  Quality Management System
  Unique in utility history
  DOE QTS
  Energy storage testing in transportation and stationary fields
  Vehicle and power train testing and evaluation
  Charging infrastructure evaluation, standards
  Fleet support

## Slide 5: SCE Transportation Electrification Programs
Authorization SB350
Charge Ready Pilot
  $22M, 1000 ports
Priority Review Projects
  Residential make ready rebates
  Transit bus
  DCFC
  Port of Long Beach crane electrification, electric yard tractors
Charge Ready Transport – $356M, 8490 ports
Novel EV Charging Tariffs – demand charge holiday, aggressive pricing
Charge Ready 2 – Filed application, $760M, 48,000 ports

## Slide 6: DCFC SI Project Objectives
Project Objectives
Characterize and understand the effects of concentrated high power EV charging loads on the SCE distribution system
Collect a data set to form the basis for grid modeling to assist distribution system planning to support future transportation electrification growth (7 million EVs, 2030)
As part of the PQ analysis, study the load factor and utilization of the charging plazas to understand coincident demand and load shapes; forecast impact with growth and input to grid planning
8 Type 2 DCFC Charging Plazas Monitored
7 Type 1 DCFC Charging Plazas Monitored

## Slide 7: DCFC SI Project Tasks
Tasks
Install power quality (PQ) equipment at 7 Type 1 and 8 Type 2 fast charger locations
Monitor 1 to 2 months depending on how long it takes to characterize the load, and what anomalies are found
Power Quality Data being Collected:
  V, I, P, RP
  Energy
  Power Factor
  Harmonics (IEEE 519 Analysis)
Utilization, Load Factor
Reliability
8 Type 2 DCFC Charging Plazas Monitored
7 Type 1 DCFC Charging Plazas Monitored

## Slide 8: Procedures: SAE J2894 Power Quality Requirements for PEV Chargers
Parameters defined in J2894/2
Procedures and System Energy Efficiency defined in SAE J2894/2™
PQ Effects on the Grid
Effects of the Grid on the System

## Slide 9: Procedures: SAE J2894 Power Quality Requirements for PEV Chargers
SAE J2894/1™
Total Power Factor (minimum) | 95%
Total Harmonic Current Distortion (max.) | 10%
Inrush Current (maximum) | 120%
Power Conversion Efficiency | 90%
Procedures and System Energy Efficiency defined in SAE J2894/2™

## Slide 10: SAE J2894 Grid Events
Momentary Outage | 0V for 12 cycles
Voltage Range Variation | 90%-110% of nominal
Voltage Sag | Down to 80% of nominal for 2 sec
Voltage Swell | 175% of nominal for Min. 1/2 cycle (8 ms)
Voltage Surge | 6 kV
Frequency Variations | 2% of nominal
Voltage Distortion | 5%

## Slide 11: Measurements
Monitoring equipment is connected to the load side of the main breaker, and monitors current and voltage.
Our monitoring equipment
Power Cabinet or Unit DCFC

## Slide 12: Sample IEEE 519 Analysis
Max (Continuous) Demand Load Current (IL)
Total Demand Distortion (TDD) is 6.56%
ISC = 5242.9 amps ISC/IL = 147
Site complies with IEEE 519
Chart: IEEE 519 Current Distortion Analysis, Odd Harmonics
| 3 | 5 | 7 | 9 | 11 | 13 | 15 | 17 | 19 | 21 | 23 | 25 | 27 | 29 | 31 | 33 | 35 | 37 | 39 | 41 | 43 | 45 | 47 | 49
Phase A | 0.047448 | 0.061432 | 0.029754 | 0.024632 | 0.011974 | 0.0067648 | 0.0033299 | 0.0031342 | 0.0018325 | 0.0010085 | 0.0011233 | 0.00094818 | 0.00061646 | 0.00071796 | 0.00064692 | 0.000423 | 0.00046763 | 0.00042064 | 0.00028756 | 0.00034116 | 0.0003009 | 0.00021405 | 0.00021824 | 0.00019734
Phase B | 0.043008 | 0.062938 | 0.036623 | 0.021256 | 0.012841 | 0.006739 | 0.0024192 | 0.003102 | 0.0017951 | 0.00075809 | 0.001001 | 0.00091884 | 0.00049056 | 0.00064186 | 0.00061095 | 0.00032925 | 0.00041929 | 0.00042244 | 0.00023259 | 0.00029475 | 0.00030414 | 0.0001759 | 0.00020283 | 0.00019617
Phase C | 0.038826 | 0.061803 | 0.036432 | 0.017972 | 0.014948 | 0.0079598 | 0.0023512 | 0.0031681 | 0.0017857 | 0.00080845 | 0.0010438 | 0.00083779 | 0.00047336 | 0.00067435 | 0.0005444 | 0.00031695 | 0.00044424 | 0.00036927 | 0.00023451 | 0.00033156 | 0.00026856 | 0.00017652 | 0.00021846 | 0.00017576
100>1000 ISC/IL Limit | 0.12 | 0.12 | 0.12 | 0.12 | 0.055 | 0.055 | 0.055 | 0.05 | 0.05 | 0.05 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Chart: IEEE 519 Current Distortion Analysis, Even Harmonics
Phase A | 0.0017322 | 0.0090647 | 0.0050776 | 0.00089759 | 0.00071178 | 0.00033 | 0.00014251 | 0.00018228 | 0.00017188 | 8.9939e-05 | 4.737e-05 | 4.8235e-05 | 3.6612e-05 | 2.8375e-05 | 3.5161e-05 | 3.2873e-05 | 3.3575e-05 | 4.592e-05 | 4.9359e-05 | 4.0839e-05 | 4.5751e-05 | 4.0321e-05 | 3.6398e-05 | 3.9018e-05
Phase B | 0.0021661 | 0.009076 | 0.0060252 | 0.0013753 | 0.00060915 | 0.00038579 | 0.00016639 | 0.00021597 | 0.00017344 | 7.7552e-05 | 3.859e-05 | 4.1389e-05 | 3.6724e-05 | 3.1864e-05 | 3.2748e-05 | 4.094e-05 | 3.1368e-05 | 3.6646e-05 | 4.2873e-05 | 3.1701e-05 | 3.6084e-05 | 3.7208e-05 | 2.4997e-05 | 2.9132e-05
Phase C | 0.0015392 | 0.00865 | 0.0053934 | 0.0011946 | 0.00071965 | 0.00028642 | 9.484e-05 | 0.0001835 | 0.00014335 | 5.7127e-05 | 4.212e-05 | 4.0355e-05 | 4.4042e-05 | 4.004e-05 | 4.1873e-05 | 3.886e-05 | 4.0996e-05 | 4.6796e-05 | 4.4222e-05 | 4.212e-05 | 4.5616e-05 | 3.8118e-05 | 3.386e-05 | 3.6297e-05
100>1000 ISC/IL Limit | 0.03 | 0.03 | 0.03 | 0.03 | 0.01375 | 0.01375 | 0.01375 | 0.0125 | 0.0125 | 0.0125 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0025

## Slide 13: High Neutral Current after Phase-Drop
High current spikes followed by high neutral currents for roughly 10 minutes when 1 or 2 of the phases drop
Events typically last around 10 minutes at all the sites, charging not interrupted
Monitored at the output of the main breaker, which means all active chargers may be behaving in a coordinated fashion
Snapshot taken at the start of the event
Snapshot taken from time indicated by red vertical line from the window to the left

## Slide 14: Neutral Currents over time
Chart: Amps
Chart: Amps
Chart: Amps
High neutral currents & phase-drop outs seems to happen somewhat periodically, but at varying magnitudes, for a consistent period of time.
49 | Neutral Current Events
8 | Average Duration (min)
1.1 | Events / Day
22 | Neutral Current Events
8 | Average Duration (min)
0.6 | Events / Day
34 | Neutral Current Events
8 | Average Duration (min)
1.1 | Events / Day

## Slide 15: Findings – Utilization, Load Factor
Subscription model stations have much higher utilization, load factor
Pay-go model stations can have low utilization
Customer owned integrated or stand-alone energy storage used for managing demand, electricity costs
How will SCE use these results for system planning?
  Effect of tariffs
  Effect of pricing

## Slide 16: Findings – Safety
Equipment ground bonding jumper removed
Safety hazard
Was this an attempt to address reliability?

## Slide 17: Summary of Findings
High neutral currents found to result at certain stations
  Neutral current behavior preceded by a high current spike
  Behavior lasts about 10 minutes
  These events occur around once per day, and could be associated with normal grid transients, such as occur with capacitor switching
  This behavior is not desirable since it could cause further tripping, causes some voltage distortion, and results in load imbalance, which may potentially impact other nearby loads and customers
  Normal grid transients – Customer must protect their own sensitive electronic systems with their own appropriate isolation, filtering, storage
Utilization driven by pricing programs, technology
  Increases sensitivity around planning
Safety
  Technology implications
  Safety inspections
  TE infrastructure project commissioning

## Slide 18: Distributed Charging Resources Project
Project in planning, to start later this year
DC Fast Charge stations or plazas with associated energy storage systems
Approximately 5 locations
Energy storage systems to be sized according to findings of DCFC SI project
Battery to be used for both load management (customer benefit) and as SCE utility system grid managed device
  Wires deferral, renewable integration, time shift, PQ
Second life element, partnership with OEMs

## Slide 19: Conclusion and Q&A
DCFC SI Publication: EPRI Case Study
Follow in EPIC proceedings
Acknowledgements:
  Andrew Ioan, Electrical Engineer
  Matt Norwalk, Power Quality Specialist
Contact:
  jordan.smith@sce.com